[image: image1.png]!

A p—T
X p—7

o

Ag—
Xp—7
Ef—
Fg—



[image: image5.png]RS ML AV ERiE: NENEA:
400-8828-058 027-83309597 027-83309626



                      

HYG-5KVA/10KV
工 频 耐 压 试 验 装 置
概述

试验变压器又称升压器，它是发电站、供配电系统及科研单位等广大用户的基本试验设备，用于对各种电气产品、电器元件、绝缘材料等进行规定电压下的绝缘强度试验，考核产品的绝缘水平，发现被试品的绝缘缺陷，衡量过电压的能力。

产品型号；HYG-5KVA/10KV
容量：5KVA ，一体式；
重量：约65kg


输入电压：200V，输入电流：25A；
输出电压：10KV，输出电流：500mA；

外形尺寸：550*400*710，
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结构

本系列产品铁芯为单相芯式，采用优质冷轧取向硅钢片叠制而成，紧固方式采用钢材作夹件。高压线圈为圆筒多层塔式，由优质聚酯漆包线及高耐压值绝缘材料绕制而成。低压线圈在外。仪表线圈为一独立绕组，一般情况下为100V。壳体为八角形，10KVA以上的试验变压器装有可移动的铁轮。具有重量轻、体积小、移动方便、性能优越等特点。

工作原理

交流、交直流试验变压器：

将工频电源输入操作箱（或操作台），经自藕调压器调节电压输入至试验变压器的初级绕组。根据电磁感应原理，在次级（高压）绕组可获得工频高压。此工频高压经高压硅堆整流及电容滤波后可获得直流高压，其幅值是交流高压有效值的1.4倍。只不过在使用直流时应抽出短路杆，在使用交流时，插入短路杆。
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Operation Specification

1.Equipment operators should be trained. Unrelated person
are prohibited from operating.
2.Before testing, pls check and ensure there is no shipping |
damage or bad contact of equipment. |
3.All grounding terminals must be connected well. Before
equipments are firmly grounded, it is not allowed to enter
the test procedure. Otherwise it will be dangerous!

4. Before operation, pls check all electrical components are
good, especially the good contact of voltage regulator
carbon brushes.

5. Plis operate in accordance with the procedures strictly.
6.This set equipments can” t be operated under over rated

parameters.
7.During the boost or withstand voltage process, if an
overcurrent such as short circuit, flashover, or

breakdown occurs, the overcurrent relay (—-KA) operates
to cut off the main circuit. Now the regulator should be
turned counterclockwise to zero.
8.After the test is completed, plis return the regulator to the
zero position and then turn off the power
9. The workplace should be free of gases, vapors, chemical
dust, other explosive and aggressive media which can
seriously affecting insulation.
10.Before the powaer is turned on, pls check and ensure: the
ground wires are reliably grounded; there is no person
around the high voltage area; the test area has a fence
(or warning line) which is guarded.
11.Pls check and ensure that the high voltage line is
suspended and stretched straight, and kept at a safe
discharge distance




交流试变原理图          交直流试变原理图

2、带抽头试验变压器：

为了同时满足一个变压器电压较高电压较小与电流较低电流较大之间的矛盾，将高压绕组分成两个来绕，一个是电流较大的绕组，另一个是电流较小的绕组，然后两个绕组串接分别引出，原理示意图如下：
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3．串级试验变压器：

为了得到更高电压的试验变压器，也可采用串级的方法获得更高的电压。图二为三级串试验变压器的原理接线图。其中三台变压器的容量和电压关系满足：P1=2P2=3P3，U（总）=U1+U2+U3S,
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串级试变原理图

四、使用注意事项

1、试验变压器应和操作箱（台）配套使用，操作箱（台）的使用方法，请详细参阅操作箱（台）使用说明书。

2、变压器外壳、高压尾必须接地。为确保安全，试验人员和其它被试验设备与试验变压器之间必须保持足够的距离。

3、试验变压器的输出一般应串接限流电阻以保护设备安全。

HYG-5KVA/10KV变压器-接线示意图:
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产品装箱单

试验变压器一台

产品说明书一份

产品合格证一份
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